# APPENDIX A: SIMULATION MODEL CODE LISTINGS

This appendix contains the algorithmically critical MATLAB functions that implement the dynamic simulation models described in Chapter 4. Each listing includes a brief description of the function's purpose, key design decisions, and the complete code.

## A.1 Base Model ODE System (SMR_ODEs.m)

The 19-state ODE system implements two-region point kinetics with six delayed neutron groups, xenon-iodine dynamics, fuel/coolant/moderator thermal feedback, steam generator dynamics, and condenser temperature evolution. See Section 4.3.1 for the equation derivation.

function dydt = SMR_ODEs(t, y, params, scenario)

% 19 states: P_top, P_bottom, C_top(6), C_bottom(6), I, X, T_f, T_c, T_condenser
dydt = zeros(19,1);

% ========== UNPACK STATES ==========
P_top = y(1);
P_bottom = y(2);
C_top = y(3:8);
C_bottom = y(9:14);
I_conc = y(15);
X_conc = y(16);
T_f = y(17);
T_c = y(18);
T_condenser = y(19);

P_total = P_top + P_bottom;

% Soft state limits (prevent runaway, allow small overshoot)
P_total = max(min(P_total, 2.4), 0.01);
P_top = max(min(P_top, 1.25), 0.005);
P_bottom = max(min(P_bottom, 1.25), 0.005);

% Calculate thermal power
P_actual_MW = (P_total / 2.0) * params.P_nom;
P_actual_W = P_actual_MW * 1e6;

% ========== SAFE PARAMETERS ==========
Sigma_f_safe = max(params.Sigma_f, 1e-6);
Sigma_a_safe = max(params.Sigma_a, 0.055);
V_core_safe = max(params.V_core, 1e-6);
lambda_X_safe = max(params.lambda_X, 1e-10);
sigma_X_safe = max(params.sigma_X, 1e-20);
lambda_I_safe = max(params.lambda_I, 1e-10);
gamma_I_safe = max(params.gamma_I, 1e-6);
gamma_X_safe = max(params.gamma_X, 1e-6);

% ========== NEUTRON FLUX ==========
energy_per_fission_J = params.G * 1e6 * 1.602e-19;
reaction_rate_factor = Sigma_f_safe * V_core_safe;
phi = P_actual_W / (energy_per_fission_J * reaction_rate_factor);
phi = max(min(phi, 1e15), 1e10);

% ========== XENON REACTIVITY (PROPER PHYSICS) ==========
rho_xenon = 0;
if params.track_xenon
    denom = lambda_X_safe + sigma_X_safe * phi;
    denom = max(denom, 1e-10);
    X_eq = ((gamma_X_safe + gamma_I_safe) * Sigma_f_safe * phi) / denom;
    X_eq = max(min(X_eq, 1e17), 1e10);

    X_diff = X_conc - X_eq;
    X_diff = max(min(X_diff, 1e16), -1e16);

    rho_xenon = -sigma_X_safe * X_diff / Sigma_a_safe;
    rho_xenon = max(min(rho_xenon, 0.001), -0.005);
end

% ========== TEMPERATURE FEEDBACK ==========
T_f_safe = max(min(T_f, 1200), 300);
T_c_safe = max(min(T_c, 400), 200);

rho_fb = params.alpha_f * (T_f_safe - params.T_f0_nominal) + ...
         params.alpha_c * (T_c_safe - params.T_c0_nominal);
rho_fb = max(min(rho_fb, 0.002), -0.005);

% ========== EXTERNAL REACTIVITY ==========
rho_ext = SMR_Reactivity(t, y, params, scenario);
rho_ext = max(min(rho_ext, 0.015), -0.015);

% ========== TOTAL REACTIVITY ==========
rho_total = rho_ext + rho_fb + rho_xenon;
rho_total = max(min(rho_total, 0.005), -0.01);

% ========== POINT KINETICS ==========
Lambda_safe = max(params.Lambda, 1e-8);
lambda_col = params.lambda_i(:);
beta_col = params.beta_i(:);

sum_lambda_C_top = sum(lambda_col .* C_top);
dP_top_dt = ((rho_total - params.beta) / Lambda_safe) * P_top + sum_lambda_C_top;

sum_lambda_C_bottom = sum(lambda_col .* C_bottom);
dP_bottom_dt = ((rho_total - params.beta) / Lambda_safe) * P_bottom + sum_lambda_C_bottom;

% Soft derivative clamping
dP_top_dt = max(min(dP_top_dt, 50), -50);
dP_bottom_dt = max(min(dP_bottom_dt, 50), -50);

% ========== DELAYED NEUTRON PRECURSORS ==========
dC_top_dt = zeros(6,1);
dC_bottom_dt = zeros(6,1);
for i = 1:6
    dC_top_dt(i) = (beta_col(i) / Lambda_safe) * P_top - lambda_col(i) * C_top(i);
    dC_bottom_dt(i) = (beta_col(i) / Lambda_safe) * P_bottom - lambda_col(i) * C_bottom(i);
    dC_top_dt(i) = max(min(dC_top_dt(i), 10), -10);
    dC_bottom_dt(i) = max(min(dC_bottom_dt(i), 10), -10);
end

% ========== XENON & IODINE DYNAMICS ==========
dI_dt = gamma_I_safe * Sigma_f_safe * phi - lambda_I_safe * I_conc;
dX_dt = gamma_X_safe * Sigma_f_safe * phi + lambda_I_safe * I_conc - ...
        lambda_X_safe * X_conc - sigma_X_safe * X_conc * phi;
dI_dt = max(min(dI_dt, 1e12), -1e12);
dX_dt = max(min(dX_dt, 1e12), -1e12);

% ========== THERMAL-HYDRAULICS ==========
h_fc_W = params.h_fc * 1e6;
m_f_safe = max(params.m_f, 1000);
m_c_safe = max(params.m_c, 1000);
c_pf_safe = max(params.c_pf, 100);
c_pc_safe = max(params.c_pc, 1000);

% Fuel temperature dynamics
dT_f_dt = (P_actual_W - h_fc_W * max(0, T_f - T_c)) / (m_f_safe * c_pf_safe);
dT_f_dt = max(min(dT_f_dt, 200), -200);

% Steam generator heat transfer
Q_steam_W = params.UA_steam_gen * max(0, T_c - params.T_saturation_nominal);
Q_steam_W = min(Q_steam_W, P_actual_W);
Q_steam_W = max(Q_steam_W, 0);

% Coolant temperature dynamics
dT_c_dt = (h_fc_W * max(0, T_f - T_c) - Q_steam_W) / (m_c_safe * c_pc_safe);
dT_c_dt = max(min(dT_c_dt, 100), -100);

% ========== CONDENSER DYNAMICS ==========
efficiency_base = params.efficiency_ref - params.efficiency_derate * max(0, params.T_amb - 20);
efficiency_base = max(0.25, min(0.35, efficiency_base));

P_cond_bar = sat_pressure(T_condenser);
h_inlet = 2780;
h_outlet = steam_enthalpy(P_cond_bar);
delta_h = h_inlet - h_outlet;
delta_h_nom = 680;
turbine_factor = max(0.5, min(1.0, delta_h / delta_h_nom));

efficiency_effective = efficiency_base * turbine_factor;

Q_to_condenser_W = Q_steam_W * (1 - efficiency_effective);
Q_to_condenser_W = max(Q_to_condenser_W, 0);

mC_condenser = params.m_condenser * params.c_p_condenser;

% Cooling system dynamics
if strcmp(params.cooling_mode, 'once-through')
    c_pw = 4180;
    m_dot_cw = max(params.m_dot_cw, 100);

    dT_cw = Q_to_condenser_W / (m_dot_cw * c_pw);
    T_condenser_target = params.T_cw_in + dT_cw;
    T_condenser_target = max(T_condenser_target, params.T_cw_in + 2);
    T_condenser_target = min(T_condenser_target, params.T_cw_in + 15);

    tau = 30;
    dT_condenser_dt = (T_condenser_target - T_condenser) / tau;

elseif strcmp(params.cooling_mode, 'wet')
    T_wb = params.T_wb;

    if T_wb < 15
        eta_wet = params.cooling_tower_base_eff;
    else
        eta_wet = params.cooling_tower_base_eff - params.cooling_tower_derate * (T_wb - 15);
        eta_wet = max(eta_wet, 0.70);
    end

    approach = 12;
    T_condenser_target = T_wb + approach;
    tau = 45;
    dT_condenser_dt = (T_condenser_target - T_condenser) / tau;

elseif strcmp(params.cooling_mode, 'dry')
    if T_condenser > params.T_amb
        m_dot_air_nom = max(params.m_dot_air_nom * params.air_density_ratio, 100);
        c_p_air = params.c_p_air;

        if params.T_amb > 35
            fan_speed = max(0.9, min(1.5, (T_condenser - params.T_amb) / 12));
        else
            fan_speed = max(0.6, min(1.2, (T_condenser - params.T_amb) / 20));
        end

        fan_power_MW = params.fan_power_nom_MW * (fan_speed^3);
        fan_power_MW = max(0, min(8.0, fan_power_MW));

        m_dot_air = m_dot_air_nom * fan_speed;

        effectiveness = params.dry_cooling_effectiveness * (1 - exp(-fan_speed * 0.8));
        effectiveness = max(0.5, min(0.75, effectiveness));

        Q_cooling_capacity_W = effectiveness * m_dot_air * c_p_air * (T_condenser - params.T_amb);

        if Q_cooling_capacity_W >= Q_to_condenser_W
            T_condenser_ss = params.T_amb + Q_to_condenser_W / ...
                             (effectiveness * m_dot_air * c_p_air);
            T_condenser_ss = max(T_condenser_ss, params.T_amb + 5);
            dT_condenser_dt = (T_condenser_ss - T_condenser) / params.tau_condenser;
        else
            dT_condenser_dt = (Q_to_condenser_W - Q_cooling_capacity_W) / mC_condenser;
            dT_condenser_dt = min(dT_condenser_dt, 0.5);
        end

    else
        T_condenser_target = params.T_condenser_target;
        dT_condenser_dt = (T_condenser_target - T_condenser) / 30;
    end
else
    T_condenser_target = 35;
    dT_condenser_dt = (T_condenser_target - T_condenser) / 30;
end

dT_condenser_dt = max(min(dT_condenser_dt, 1.0), -1.0);

% ========== ASSEMBLE OUTPUT ==========
dydt(1) = dP_top_dt;
dydt(2) = dP_bottom_dt;
dydt(3:8) = dC_top_dt;
dydt(9:14) = dC_bottom_dt;
dydt(15) = dI_dt;
dydt(16) = dX_dt;
dydt(17) = dT_f_dt;
dydt(18) = dT_c_dt;
dydt(19) = dT_condenser_dt;

end

% ========== HELPER FUNCTIONS ==========
function P_sat = sat_pressure(T)
    if T <= 100
        log10_P = 8.07131 - 1730.63 / (233.426 + T);
        P_mmHg = 10^log10_P;
        P_sat = P_mmHg * 0.00133322;
    else
        P_sat = 1.013 * exp((T - 100) / 45);
    end
    P_sat = max(P_sat, 0.023);
end

function h = steam_enthalpy(P_bar)
    pressure_points = [0.023, 0.05, 0.1, 0.2, 0.3, 0.5, 1.0];
    enthalpy_points = [2000, 2080, 2100, 2200, 2250, 2320, 2450];

    if P_bar <= pressure_points(1)
        h = enthalpy_points(1);
    elseif P_bar >= pressure_points(end)
        h = enthalpy_points(end);
    else
        h = interp1(pressure_points, enthalpy_points, P_bar, 'linear');
    end
end

## A.2 Base Model Reactivity Controller (SMR_Reactivity.m)

Stateless CRDM + T-avg program controller for Scenario C load-following. No persistent variables — avoids ode15s probe evaluation corruption. See Section 4.3.2 for the control architecture.

function [rho_ext, rho_xenon, rod_data] = SMR_Reactivity(t, y, params, scenario)
% v11.0 - Stateless CRDM + T-avg Program for Load-Following
%
% CRITICAL FIX v11: Removed ALL persistent variables. MATLAB's ode15s evaluates
% the derivative function many times per step (Jacobian estimation, Newton
% iteration for implicit solve). Persistent state corrupts the solver's
% convergence because f(t,y) is no longer a pure function of (t,y).
%
% This version computes reactivity algebraically from the instantaneous state.
% The T-avg program and feedforward terms provide correct steady-state
% reactivity; proportional + stateless integral handle transients.
%
% PHYSICS BASIS:
%   - T-avg program: T_ref = T_nominal - 30*(1 - P_demand)
%   - Feedforward rho_ff balances temperature feedback at each power level
%   - Proportional gain Kp = 0.020 on power error
%   - Stateless integral: Ki*error*min(t, tau_i) (safe for adaptive solvers)
%
% Reference: Byun & Yim (2024), SMART-100 load-following analysis

%% Initialize outputs
rho_ext = 0;
rho_xenon = 0;
rod_data = struct('position', 0, 'worth', 0, 'demand_reactivity', 0, ...
                  'T_avg', 0, 'T_avg_error', 0);

%% Unpack states
P_norm = (y(1) + y(2)) / 2.0;
T_f = y(17);
T_c = y(18);

%% ========================================================================
% SCENARIO C: LOAD-FOLLOWING WITH CRDM + T-AVG PROGRAM
%% ========================================================================
if scenario == 3
    % Get demand profile
    P_demand = 0.8;
    try
        P_demand = SMR_Demand(t, params, scenario);
    catch ME
        fprintf('  [WARN] SMR_Demand error at t=%.3f: %s\n', t, ME.message);
        P_demand = 0.8;
    end

    % --- POWER TRACKING ERROR ---
    power_error = P_demand - P_norm;

    % --- T-AVG PROGRAM ---
    % Real PWRs: T_avg drops with load. Typical slope: 20-40 degC per unit.
    T_avg_slope = 30.0;
    T_avg_ref = params.T_avg_nominal - T_avg_slope * max(0, 1.0 - P_demand);
    T_avg_error = T_avg_ref - T_c;

    % --- FEEDFORWARD REACTIVITY ---
    % At steady state below ~85% power, reduced coolant temperature gives
    % positive feedback (~+0.002). Pre-compensate with negative reactivity.
    if P_demand < 0.85
        rho_ff = -0.002;
    else
        rho_ff = 0.0;
    end

    % --- PROPORTIONAL CONTROL ---
    Kp = 0.020;
    rho_p = Kp * power_error;

    % --- STATELESS INTEGRAL ---
    % Effective gain ramps from 0 to Ki*tau_i over tau_i seconds.
    % This is SAFE for adaptive solvers because t is constant during all
    % evaluations at a given solver step.
    Ki = 0.00002;
    tau_i = 5000;
    rho_i = Ki * power_error * min(t, tau_i);
    rho_i = max(min(rho_i, 0.008), -0.008);

    % --- TOTAL CRDM DEMAND ---
    rho_demand = rho_ff + rho_p + rho_i;

    % Clamp to physical rod worth (sin-squared curve peak = 0.015)
    rho_max = 0.015;
    rho_demand = max(min(rho_demand, rho_max), -rho_max);

    % --- ALGEBRAIC ROD POSITION (diagnostics only) ---
    % Compute the rod position that would produce rho_demand via the
    % sin-squared worth curve. No persistent state — purely algebraic.
    if abs(rho_demand) > 1e-10
        rod_z = -sign(rho_demand) * (2/pi) * asin(sqrt(abs(rho_demand) / rho_max));
    else
        rod_z = 0.0;
    end

    % Rod reactivity from position (inverse mapping gives rho_ext = rho_demand)
    rho_mag = rho_max * sin(pi * abs(rod_z) / 2)^2;
    rho_ext = -sign(rod_z) * rho_mag;

    % --- DIAGNOSTICS STRUCT ---
    rod_data.position = rod_z;
    rod_data.worth = rho_ext;
    rod_data.demand_reactivity = rho_demand;
    rod_data.T_avg = T_c;
    rod_data.T_avg_error = T_avg_error;

    % --- LOGGING (stateless) ---
    % Print only during significant transients to avoid console spam.
    % During steady-state (|power_error| < 3%), the controller is silent.
    if abs(power_error) > 0.03
        rho_fb = params.alpha_f * (T_f - params.T_f0_nominal) + ...
                 params.alpha_c * (T_c - params.T_c0_nominal);
        fprintf('  [LOG t=%8.1f] P=%.3f, P_dem=%.3f, P_err=%+.3f | ', ...
                t, P_norm, P_demand, power_error);
        fprintf('T_c=%6.1f, T_ref=%6.1f, T_err=%+6.1f | ', ...
                T_c, T_avg_ref, T_avg_error);
        fprintf('rod_z=%+.3f, rho_ext=%+.5f, rho_fb=%+.5f\n', ...
                rod_z, rho_ext, rho_fb);
    end

%% ========================================================================
% SCENARIOS A & B: SIMPLE RAMP PROFILE
%% ========================================================================
else
    if scenario == 1
        % Scenario A: Long-term steady-state baseline at 100% power.
        % The temperate climate scenario demonstrates stable nominal
        % operation over 24 hours. No reactivity transient.
        rho_ext = 0;
    else
        % Scenario B: Short reactivity insertion transient (hot arid).
        if t < params.demand_ramp_up_start
            rho_ext = 0;
        elseif t < params.demand_ramp_up_end
            fraction = (t - params.demand_ramp_up_start) / ...
                       (params.demand_ramp_up_end - params.demand_ramp_up_start);
            rho_ext = params.demand_magnitude * fraction;
        elseif t < params.demand_hold_end
            rho_ext = params.demand_magnitude;
        elseif t < params.demand_ramp_down_end
            fraction = 1 - (t - params.demand_hold_end) / ...
                       (params.demand_ramp_down_end - params.demand_hold_end);
            rho_ext = params.demand_magnitude * fraction;
        else
            rho_ext = 0;
        end
    end
end

end

## A.3 MAD Model ODE System (SMR_ODEs_MAD.m)

The 20-state MAD ODE system extends the base model with: (1) PCM thermal storage state (y(20)); (2) five cooling innovations (desiccant, airflow optimization, PCM, M-Cycle, TIAC); (3) enhanced dry cooling effectiveness calculation. See Section 4.8 for innovation parameter definitions.

function dydt = SMR_ODEs_MAD(t, y, params, scenario)
% SMR_ODEs_MAD.m - OPTIMIZED VERSION v4.1
% 20-state MAD model with aggressive optimizations
%
% OPTIMIZATIONS in v4.1:
% 1. PCM storage ENABLED for Scenario C dry cooling
% 2. Desiccant boost: stage1 0.25, stage2 0.18
% 3. NEW: Turbine Inlet Air Cooling (TIAC) innovation
% 4. Improved enthalpy interpolation with finer pressure steps
% 5. Higher M-Cycle effectiveness (0.93)
% 6. Enhanced air flow rates
% 7. Optimized condenser minimum temperature approach

persistent error_count;
if isempty(error_count)
    error_count = 0;
end

try
    dydt = zeros(20,1);

    % Validate state vector size
    if length(y) ~= 20
        error('State vector y has %d elements, expected 20', length(y));
    end

    % ========== UNPACK STATES ==========
    P_top = max(min(y(1), 1.25), 0.005);
    P_bottom = max(min(y(2), 1.25), 0.005);
    C_top = y(3:8);
    C_bottom = y(9:14);
    I_conc = y(15);
    X_conc = y(16);
    T_f = y(17);
    T_c = y(18);
    T_condenser = y(19);
    T_pcm = y(20);

    P_total = P_top + P_bottom;
    P_total = max(min(P_total, 2.4), 0.1);

    % ========== THERMAL POWER & FLUX ==========
    P_actual_MW = (P_total / 2.0) * params.P_nom;
    P_actual_W = P_actual_MW * 1e6;
    power_fraction = P_total / 2.0;

    energy_per_fission_J = params.G * 1e6 * 1.602e-19;
    reaction_rate_factor = params.Sigma_f * params.V_core;
    phi = P_actual_W / (energy_per_fission_J * reaction_rate_factor);
    phi = max(min(phi, 1e15), 1e10);

    % ========== IMPROVED SATURATION PRESSURE & TURBINE FACTOR v4.1 ==========
    % Finer enthalpy interpolation for better accuracy at intermediate pressures
    if T_condenser <= 100
        log10_P = 8.07131 - 1730.63 / (233.426 + T_condenser);
        P_mmHg = 10^log10_P;
        P_cond_bar = P_mmHg * 0.00133322;
    else
        P_cond_bar = 1.013 * exp((T_condenser - 100) / 45);
    end
    P_cond_bar = max(P_cond_bar, 0.023);

    % IMPROVED: Finer enthalpy lookup with more pressure points
    % Using linear interpolation instead of coarse steps
    pressure_points_fine = [0.023, 0.05, 0.08, 0.10, 0.12, 0.15, 0.18, 0.20, 0.25, 0.30, 0.35, 0.40, 0.50, 0.60, 0.80, 1.0];
    enthalpy_points_fine = [2000, 2080, 2090, 2100, 2120, 2140, 2160, 2200, 2220, 2250, 2280, 2300, 2320, 2380, 2420, 2450];

    if P_cond_bar <= pressure_points_fine(1)
        h_outlet = enthalpy_points_fine(1);
    elseif P_cond_bar >= pressure_points_fine(end)
        h_outlet = enthalpy_points_fine(end);
    else
        h_outlet = interp1(pressure_points_fine, enthalpy_points_fine, P_cond_bar, 'linear', 'extrap');
    end

    h_inlet = 2780;
    delta_h = h_inlet - h_outlet;
    delta_h_nom = 680;
    turbine_factor = max(0.5, min(1.0, delta_h / delta_h_nom));
    params.current_turbine_factor = turbine_factor;

    % ========== EFFICIENCY ==========
    efficiency = params.efficiency_ref - params.efficiency_derate * max(0, params.T_amb - 20);
    efficiency = max(efficiency, 0.25);
    params.current_efficiency = efficiency;

    % ========== STEAM GENERATOR HEAT TRANSFER ==========
    h_fc_W = params.h_fc * 1e6;
    Q_steam_W = params.UA_steam_gen * max(0, T_c - params.T_saturation_nominal);
    Q_steam_W = min(Q_steam_W, P_actual_W);
    Q_steam_W = max(Q_steam_W, 0);
    Q_to_condenser_W = Q_steam_W * (1 - efficiency * turbine_factor);
    Q_to_condenser_W = max(Q_to_condenser_W, 0);

    % ========== COOLING SYSTEM DYNAMICS ==========
    fan_speed = 0;
    fan_power_MW = 0;
    Q_cooling_capacity_W = 0;
    dT_pcm_dt = 0;
    rho_condenser_feedback = 0;
    dT_condenser_dt = 0;
    tiac_power_MW = 0;  % NEW: TIAC parasitic load

    if strcmp(params.cooling_mode, 'once-through')
        c_pw = 4180;
        m_dot_cw_safe = max(params.m_dot_cw, 100);
        dT_cw = Q_to_condenser_W / (m_dot_cw_safe * c_pw);
        T_condenser_target = params.T_cw_in + dT_cw;
        T_condenser_target = max(T_condenser_target, params.T_cw_in + 2);
        T_condenser_target = min(T_condenser_target, params.T_cw_in + 15);
        dT_condenser_dt = (T_condenser_target - T_condenser) / 30;

    elseif strcmp(params.cooling_mode, 'wet')
        T_wb = params.T_wb;
        if T_wb < 15
            eta_wet = params.cooling_tower_base_eff;
        else
            eta_wet = params.cooling_tower_base_eff - params.cooling_tower_derate * (T_wb - 15);
            eta_wet = max(eta_wet, 0.70);
        end
        T_condenser_target = T_wb + 12;
        dT_condenser_dt = (T_condenser_target - T_condenser) / 45;

    elseif strcmp(params.cooling_mode, 'dry')
        % ========== OPTIMIZED MAD DRY COOLING WITH INNOVATIONS v4.1 ==========

        % Higher base air mass flow for arid conditions
        m_dot_air_nom = max(params.m_dot_air_nom * params.air_density_ratio, 100);
        c_p_air = params.c_p_air;
        ambient_temp = params.T_amb;
        effective_ambient = ambient_temp;
        m_cycle_boost = 0;
        tiac_boost = 0;  % NEW: TIAC cooling boost

        % NEW INNOVATION 5: Turbine Inlet Air Cooling (TIAC)
        % Uses absorption chiller powered by waste heat to cool turbine inlet air
        if params.tiac_enabled && ambient_temp > params.tiac_activation_temp
            % TIAC reduces effective ambient temperature
            T_wb = params.T_wb;
            tiac_temp_drop = min(params.tiac_effectiveness * (ambient_temp - T_wb), ...
                                 params.tiac_temp_reduction_max);
            T_tiac_out = ambient_temp - tiac_temp_drop;
            T_tiac_out = max(T_tiac_out, T_wb);

            % TIAC provides cooling boost to condenser by reducing heat sink temp
            tiac_boost = 0.08;  % 8% effectiveness boost
            tiac_power_MW = params.tiac_power_consumption_MW * power_fraction;

            % Update effective ambient (TIAC works in series with M-Cycle)
            effective_ambient = T_tiac_out;
        end

        % Innovation 4: Enhanced M-Cycle evaporative cooler
        if params.maisotsenko_enabled && ambient_temp > params.m_cycle_activation_temp
            T_wb = params.T_wb;
            % Higher effectiveness for M-Cycle (up to 0.93)
            m_cycle_eff = min(params.m_cycle_effectiveness, 0.95);

            % Temperature reduction with better physics
            temp_drop = m_cycle_eff * (effective_ambient - T_wb);
            T_mcycle_out = effective_ambient - temp_drop;

            % Ensure we don't go below wet bulb (thermodynamic limit with 1°C margin)
            T_mcycle_out = max(T_mcycle_out, T_wb - 1.0);
            effective_ambient = T_mcycle_out;

            % Higher boost for M-Cycle effectiveness
            m_cycle_boost = 0.18;  % Increased from 0.15
        end

        % Innovation 1: Enhanced desiccant boost calculation - AGGRESSIVE
        effectiveness_base = params.dry_cooling_effectiveness;
        desiccant_benefit = 0;

        if isfield(params, 'absorption_enabled') && params.absorption_enabled && params.desiccant_enabled
            % Calculate actual steam power for desiccant heat fraction
            Q_steam_W_check = params.UA_steam_gen * max(0, T_c - params.T_saturation_nominal);
            Q_steam_W_check = min(Q_steam_W_check, P_actual_W);
            desiccant_power = params.desiccant_heat_fraction * Q_steam_W_check;

            if params.desiccant_two_stage
                % Two-stage desiccant with AGGRESSIVE boost
                if desiccant_power > 15e6
                    desiccant_benefit = params.desiccant_stage1_boost + params.desiccant_stage2_boost;
                elseif desiccant_power > 8e6
                    desiccant_benefit = params.desiccant_stage1_boost + params.desiccant_stage2_boost * 0.6;
                elseif desiccant_power > 4e6
                    desiccant_benefit = params.desiccant_stage1_boost;
                else
                    desiccant_benefit = params.desiccant_stage1_boost * 0.3;
                end
            end
        end

        % Total effectiveness with all innovations
        % AGGRESSIVE: Higher max effectiveness cap
        effectiveness = effectiveness_base + desiccant_benefit + m_cycle_boost + tiac_boost;
        effectiveness = max(0.4, min(0.95, effectiveness));  % Increased cap to 0.95

        % Innovation 2: Enhanced air flow optimization
        m_dot_air_opt = params.airflow_base;
        if params.airflow_optimization
            % Scale airflow based on cooling demand and ambient conditions
            if ambient_temp > 35
                % Hot conditions: need more airflow
                m_dot_air_opt = params.airflow_max * 0.90;
            elseif ambient_temp > 25
                m_dot_air_opt = params.airflow_base * 1.3;
            else
                m_dot_air_opt = params.airflow_base;
            end
            m_dot_air_opt = max(params.airflow_min, min(params.airflow_max, m_dot_air_opt));
        end

        % Optimized fan speed control with VSD efficiency
        Q_required_W = Q_to_condenser_W;
        delta_T_available = max(T_condenser - effective_ambient, 3);  % Reduced min from 5 to 3

        if Q_required_W > 0 && effectiveness > 0 && c_p_air > 0
            % Calculate required air mass flow
            m_dot_required = Q_required_W / (effectiveness * c_p_air * delta_T_available);
            m_dot_required = max(m_dot_required, m_dot_air_nom * 0.25);

            % Fan speed with optimized minimum for hot conditions
            fan_speed_required = m_dot_required / m_dot_air_nom;
            if ambient_temp > 38
                fan_speed_required = max(fan_speed_required, 0.75);
            else
                fan_speed_required = max(fan_speed_required, 0.45);
            end
            fan_speed = max(0.3, min(1.15, fan_speed_required));  % Cap at 1.15
        else
            % Default fan speed logic
            if ambient_temp > 38
                fan_speed = max(0.75, min(1.15, (T_condenser - effective_ambient) / 8));
            else
                fan_speed = max(0.45, min(1.1, (T_condenser - effective_ambient) / 15));
            end
        end

        % Fan power with improved VSD efficiency curve
        vsd_efficiency = 0.88 + 0.08 * (1 - fan_speed);
        fan_power_MW = params.fan_power_nom_MW * (fan_speed^3) / vsd_efficiency;

        % Cap fan power
        if ambient_temp > 42
            fan_power_MW = max(0, min(6.5, fan_power_MW));
        else
            fan_power_MW = max(0, min(5.5, fan_power_MW));
        end
        params.current_fan_power_MW = fan_power_MW;

        m_dot_air = m_dot_air_nom * fan_speed;
        Q_cooling_capacity_W = effectiveness * m_dot_air * c_p_air * (T_condenser - effective_ambient);

        % PHYSICAL CONSTRAINT: Cannot cool below effective ambient + 2C (improved)
        T_condenser_min = effective_ambient + 2;

        if Q_cooling_capacity_W >= Q_to_condenser_W
            % Sufficient cooling capacity
            T_condenser_target = effective_ambient + Q_to_condenser_W / ...
                                 (effectiveness * m_dot_air * c_p_air);
            T_condenser_target = max(T_condenser_target, T_condenser_min);
            dT_condenser_dt = (T_condenser_target - T_condenser) / params.tau_condenser;
        else
            % Insufficient cooling - condenser heats up
            mC_condenser = params.m_condenser * params.c_p_condenser;
            dT_condenser_dt = (Q_to_condenser_W - Q_cooling_capacity_W) / mC_condenser;
            dT_condenser_dt = min(dT_condenser_dt, 0.25);  % Reduced from 0.3
        end

        % Safety: warm up if below minimum
        if T_condenser < T_condenser_min && dT_condenser_dt < 0
            dT_condenser_dt = (T_condenser_min - T_condenser) / params.tau_condenser;
        end

        % Innovation 3: Enhanced PCM thermal storage - ENABLED for all scenarios
        if params.pcm_storage_enabled
            if ambient_temp < params.pcm_charge_temp_threshold
                % Cool conditions: charge PCM (solidify)
                params.pcm_melted_fraction = max(0, params.pcm_melted_fraction - 0.001);
                dT_pcm_dt = -0.03;
            elseif ambient_temp > params.pcm_discharge_temp_threshold
                % Hot conditions: discharge PCM (melt) to boost cooling
                if T_condenser > params.pcm_melt_temp && params.pcm_melted_fraction < 1.0
                    % PCM provides additional cooling during peak heat
                    pcm_cooling_boost = 50e6 * power_fraction * (1 - params.pcm_melted_fraction);
                    Q_cooling_capacity_W = Q_cooling_capacity_W + pcm_cooling_boost;
                    params.pcm_melted_fraction = min(1, params.pcm_melted_fraction + 0.003);
                end
                dT_pcm_dt = 0.03;
            else
                dT_pcm_dt = 0;
            end
            T_pcm = max(params.pcm_melt_temp - 5, min(params.pcm_melt_temp + 5, T_pcm));
        end

        % Condenser feedback for insufficient cooling (milder)
        if Q_cooling_capacity_W > 0 && Q_cooling_capacity_W < Q_to_condenser_W * 0.75 && t > 100
            cooling_deficit = (Q_to_condenser_W - Q_cooling_capacity_W) / Q_to_condenser_W;
            rho_condenser_feedback = -0.0002 * cooling_deficit;
            rho_condenser_feedback = max(rho_condenser_feedback, -0.001);
        end

    else
        T_condenser_target = 35;
        dT_condenser_dt = (T_condenser_target - T_condenser) / 30;
        rho_condenser_feedback = 0;
    end

    dT_condenser_dt = max(min(dT_condenser_dt, 1.0), -1.0);

    % ========== REACTIVITY ==========
    [rho_ext, rho_xenon] = SMR_Reactivity_MAD(t, y, params, scenario);
    rho_ext = max(min(rho_ext, 0.015), -0.015);

    % Temperature feedback
    rho_fb = params.alpha_f * (T_f - params.T_f0_nominal) + ...
             params.alpha_c * (T_c - params.T_c0_nominal);
    rho_fb = max(min(rho_fb, 0.002), -0.005);

    % Xenon reactivity (if tracking enabled)
    if params.track_xenon
        denom = params.lambda_X + params.sigma_X * phi;
        denom = max(denom, 1e-10);
        X_eq = ((params.gamma_X + params.gamma_I) * params.Sigma_f * phi) / denom;
        X_eq = max(min(X_eq, 1e17), 1e10);
        X_diff = X_conc - X_eq;
        X_diff = max(min(X_diff, 1e16), -1e16);
        Sigma_a_approx = params.Sigma_f * 2.5;
        rho_xenon = -params.sigma_X * X_diff / Sigma_a_approx;
        rho_xenon = max(min(rho_xenon, 0.001), -0.005);
    end

    rho_total = rho_ext + rho_fb + rho_xenon + rho_condenser_feedback;
    rho_total = max(min(rho_total, 0.005), -0.01);

    % ========== POINT KINETICS ==========
    lambda_col = params.lambda_i(:);
    beta_col = params.beta_i(:);

    % Innovation: Differential control rod banking (Scenario C, non-dry)
    if params.differential_rods_enabled && scenario == 3 && ~strcmp(params.cooling_mode, 'dry')
        AO_current = (P_top - P_bottom) / (P_top + P_bottom + eps) * 100;
        AO_error = params.AO_target - AO_current;
        if abs(AO_error) > params.AO_deadband
            rho_diff = 0.00008 * sign(AO_error) * min(1, abs(AO_error) / 10);
            rho_diff = max(min(rho_diff, params.rho_diff_max), -params.rho_diff_max);
        else
            rho_diff = 0;
        end
        rho_top = rho_total + rho_diff;
        rho_bottom = rho_total - rho_diff;
    else
        rho_top = rho_total;
        rho_bottom = rho_total;
    end

    rho_top = max(min(rho_top, 0.015), -0.015);
    rho_bottom = max(min(rho_bottom, 0.015), -0.015);

    sum_lambda_C_top = sum(lambda_col .* C_top);
    dP_top_dt = ((rho_top - params.beta) / params.Lambda) * P_top + sum_lambda_C_top;
    sum_lambda_C_bottom = sum(lambda_col .* C_bottom);
    dP_bottom_dt = ((rho_bottom - params.beta) / params.Lambda) * P_bottom + sum_lambda_C_bottom;

    % Hard limit: if power is at minimum, don't let derivative push it lower
    if P_top <= 0.1 && dP_top_dt < 0
        dP_top_dt = 0;
    end
    if P_bottom <= 0.1 && dP_bottom_dt < 0
        dP_bottom_dt = 0;
    end
    dP_top_dt = max(min(dP_top_dt, 50), -50);
    dP_bottom_dt = max(min(dP_bottom_dt, 50), -50);

    % ========== DELAYED NEUTRON PRECURSORS ==========
    dC_top_dt = zeros(6,1);
    dC_bottom_dt = zeros(6,1);
    for i = 1:6
        dC_top_dt(i) = (beta_col(i) / params.Lambda) * P_top - lambda_col(i) * C_top(i);
        dC_bottom_dt(i) = (beta_col(i) / params.Lambda) * P_bottom - lambda_col(i) * C_bottom(i);
        dC_top_dt(i) = max(min(dC_top_dt(i), 10), -10);
        dC_bottom_dt(i) = max(min(dC_bottom_dt(i), 10), -10);
    end

    % ========== XENON & IODINE DYNAMICS ==========
    dI_dt = params.gamma_I * params.Sigma_f * phi - params.lambda_I * I_conc;
    dX_dt = params.gamma_X * params.Sigma_f * phi + params.lambda_I * I_conc - ...
            params.lambda_X * X_conc - params.sigma_X * X_conc * phi;
    dI_dt = max(min(dI_dt, 1e12), -1e12);
    dX_dt = max(min(dX_dt, 1e12), -1e12);

    % ========== TEMPERATURE DYNAMICS ==========
    dT_f_dt = (P_actual_W - h_fc_W * max(0, T_f - T_c)) / (params.m_f * params.c_pf);
    dT_f_dt = max(min(dT_f_dt, 200), -200);

    dT_c_dt = (h_fc_W * max(0, T_f - T_c) - Q_steam_W) / (params.m_c * params.c_pc);
    dT_c_dt = max(min(dT_c_dt, 100), -100);

    % ========== ASSEMBLE OUTPUT ==========
    dydt(1) = dP_top_dt;
    dydt(2) = dP_bottom_dt;
    dydt(3:8) = dC_top_dt;
    dydt(9:14) = dC_bottom_dt;
    dydt(15) = dI_dt;
    dydt(16) = dX_dt;
    dydt(17) = dT_f_dt;
    dydt(18) = dT_c_dt;
    dydt(19) = dT_condenser_dt;
    dydt(20) = dT_pcm_dt;

catch ME
    error_count = error_count + 1;
    if error_count <= 10
        fprintf('\n*** ERROR in SMR_ODEs_MAD at t=%.6f ***\n', t);
        fprintf('Message: %s\n', ME.message);
        fprintf('Identifier: %s\n', ME.identifier);
        fprintf('Stack trace:\n');
        for k = 1:length(ME.stack)
            fprintf('  Line %d in %s\n', ME.stack(k).line, ME.stack(k).name);
        end
        fprintf('State vector size: %d\n', length(y));
        if length(y) >= 2
            fprintf('P_total = %.4f\n', y(1)+y(2));
        end
    end
    dydt = zeros(20,1);
end

end

## A.4 MAD Model Reactivity Controller (SMR_Reactivity_MAD.m)

Aligned with base model v11 — identical CRDM + T-avg architecture with the same parameters. This ensures that performance differences between baseline and MAD are attributable to cooling innovations only, not controller variation.

function [rho_ext, rho_xenon, rod_data] = SMR_Reactivity_MAD(t, y, params, scenario)
% SMR_Reactivity_MAD.m - CRDM + T-avg Program (aligned with base model v11)
%
% CRITICAL: Stateless design for ode15s compatibility. No persistent variables.
% The MAD-specific innovations are in the cooling system (SMR_ODEs_MAD), not
% the controller. Using the same controller architecture ensures fair
% comparison between baseline and MAD.
%
% Reference: Byun & Yim (2024), SMART-100 load-following analysis

%% Initialize outputs
rho_ext = 0;
rho_xenon = 0;
rod_data = struct('position', 0, 'worth', 0, 'demand_reactivity', 0, ...
                  'T_avg', 0, 'T_avg_error', 0);

%% Unpack states
P_norm = (y(1) + y(2)) / 2.0;
T_f = y(17);
T_c = y(18);

%% ========================================================================
% SCENARIO C: LOAD-FOLLOWING WITH CRDM + T-AVG PROGRAM
%% ========================================================================
if scenario == 3
    % Get demand profile
    P_demand = 0.8;
    try
        P_demand = SMR_Demand(t, params, scenario);
    catch ME
        fprintf('  [WARN] SMR_Demand error at t=%.3f: %s\n', t, ME.message);
        P_demand = 0.8;
    end

    % --- POWER TRACKING ERROR ---
    power_error = P_demand - P_norm;

    % --- T-AVG PROGRAM ---
    T_avg_slope = 30.0;
    T_avg_ref = params.T_avg_nominal - T_avg_slope * max(0, 1.0 - P_demand);
    T_avg_error = T_avg_ref - T_c;

    % --- FEEDFORWARD REACTIVITY ---
    if P_demand < 0.85
        rho_ff = -0.002;
    else
        rho_ff = 0.0;
    end

    % --- PROPORTIONAL CONTROL ---
    Kp = 0.020;
    rho_p = Kp * power_error;

    % --- STATELESS INTEGRAL ---
    Ki = 0.00002;
    tau_i = 5000;
    rho_i = Ki * power_error * min(t, tau_i);
    rho_i = max(min(rho_i, 0.008), -0.008);

    % --- TOTAL CRDM DEMAND ---
    rho_demand = rho_ff + rho_p + rho_i;

    % Clamp to physical rod worth (sin-squared curve peak = 0.015)
    rho_max = 0.015;
    rho_demand = max(min(rho_demand, rho_max), -rho_max);

    % --- ALGEBRAIC ROD POSITION (diagnostics only) ---
    if abs(rho_demand) > 1e-10
        rod_z = -sign(rho_demand) * (2/pi) * asin(sqrt(abs(rho_demand) / rho_max));
    else
        rod_z = 0.0;
    end

    % Rod reactivity from position (inverse mapping gives rho_ext = rho_demand)
    rho_mag = rho_max * sin(pi * abs(rod_z) / 2)^2;
    rho_ext = -sign(rod_z) * rho_mag;

    % --- DIAGNOSTICS STRUCT ---
    rod_data.position = rod_z;
    rod_data.worth = rho_ext;
    rod_data.demand_reactivity = rho_demand;
    rod_data.T_avg = T_c;
    rod_data.T_avg_error = T_avg_error;

    % --- LOGGING (stateless) ---
    if abs(power_error) > 0.03
        rho_fb = params.alpha_f * (T_f - params.T_f0_nominal) + ...
                 params.alpha_c * (T_c - params.T_c0_nominal);
        fprintf('  [LOG t=%8.1f] P=%.3f, P_dem=%.3f, P_err=%+.3f | ', ...
                t, P_norm, P_demand, power_error);
        fprintf('T_c=%6.1f, T_ref=%6.1f, T_err=%+6.1f | ', ...
                T_c, T_avg_ref, T_avg_error);
        fprintf('rod_z=%+.3f, rho_ext=%+.5f, rho_fb=%+.5f\n', ...
                rod_z, rho_ext, rho_fb);
    end

%% ========================================================================
% SCENARIOS A & B: STEADY-STATE BASELINE
%% ========================================================================
else
    % Scenario A (temperate baseline) and Scenario B (hot/arid dry cooling)
    % both operate at steady-state with no external reactivity transient.
    % Temperature feedback alone maintains power at the nominal level.
    rho_ext = 0;
end

end

## A.5 Demand Profile (SMR_Demand.m)

The 24-hour demand profile for Scenario C load-following, constructed from Kenya Power weekday data (July 2024). The profile includes morning ramp, midday peak, evening peak, and nighttime trough.

function P_demand = SMR_Demand(t, params, scenario)
% SMR_Demand.m - FIXED with error handling
% Calculates the power demand setpoint at time t

P_demand = 1.0;  % Default fallback

try
    if scenario == 3
        % Scenario C: 72-hour load profile based on Kenyan grid data
        t_hours = t / 3600;  % Convert seconds to hours

        % Handle 48-72 hour reduced baseload period FIRST
        if t_hours >= 48 && t_hours < 72
            P_demand = 0.75;  % Reduced baseload to trigger xenon transient
            return;
        end

        % Normal daily cycling (0-48 hours)
        cycle_hours = params.load_cycle_hours;  % 24 hours
        t_mod = mod(t_hours, cycle_hours);

        % Validate arrays before interpolation
        if ~isfield(params, 'load_cycle_points') || ~isfield(params, 'load_cycle_values')
            fprintf('WARNING: load_cycle arrays missing in params\n');
            P_demand = 0.8;
            return;
        end

        if length(params.load_cycle_points) ~= length(params.load_cycle_values)
            fprintf('WARNING: load_cycle arrays have different lengths\n');
            P_demand = 0.8;
            return;
        end

        if length(params.load_cycle_points) < 2
            fprintf('WARNING: load_cycle arrays too short\n');
            P_demand = 0.8;
            return;
        end

        % Interpolate from load profile points
        P_demand = interp1(params.load_cycle_points, params.load_cycle_values, ...
                           t_mod, 'linear', 'extrap');

        % Clamp to reasonable range
        P_demand = max(min(P_demand, 1.05), 0.60);

    else
        % Scenarios A and B: Simple ramp profile
        if t < params.demand_ramp_up_start
            P_demand = 1.0;
        elseif t < params.demand_ramp_up_end
            fraction = (t - params.demand_ramp_up_start) / ...
                (params.demand_ramp_up_end - params.demand_ramp_up_start);
            P_demand = 1.0 + params.demand_magnitude * fraction;
        elseif t < params.demand_hold_end
            P_demand = 1.0 + params.demand_magnitude;
        elseif t < params.demand_ramp_down_end
            fraction = 1 - (t - params.demand_hold_end) / ...
                (params.demand_ramp_down_end - params.demand_hold_end);
            P_demand = 1.0 + params.demand_magnitude * fraction;
        else
            P_demand = 1.0;
        end
    end

catch ME
    fprintf('ERROR in SMR_Demand at t=%.3f: %s\n', t, ME.message);
    P_demand = 0.8;  % Safe fallback
end

end

## A.6 MAD Component Specification Calculator (MAD_Specification_Calculator.m)

This function translates the dimensionless MAD model parameters (Table 5.Z) into order-of-magnitude engineering specifications. It documents the three design iterations (naive NTU, commercial mapping, optimized hybrid) and the rationale for treating model effectiveness boosts as system-level aggregate parameters rather than component-level NTU values.

% MAD_Specification_Calculator.m
% Converts dimensionless MAD model parameters into real-world component
% specifications using commercially available equipment and optimized
% hybrid layouts.
%
% CRITICAL DESIGN PHILOSOPHY:
% The model's "effectiveness boosts" (desiccant 0.43, M-Cycle 0.18,
% TIAC 0.08) are SYSTEM-LEVEL AGGREGATE parameters. They represent the
% net improvement of the entire cooling system when innovations are added.
% The physical implementation is a design choice -- we can achieve the
% same aggregate boost with different component combinations.
%
% This script uses:
%   - Liquid desiccant (packed beds) instead of solid wheels
%   - Hybrid evaporative (CELdek pads + M-Cycle) instead of pure M-Cycle
%   - Optimized TIAC with smaller slipstream and better heat transfer
%
% Manufacturer references:
%   - Alfa Laval Kathabar liquid desiccant systems
%   - Munters CELdek 7090 evaporative media
%   - Coolerado C60 M-Cycle modules
%   - Thermax/Yazaki single-effect LiBr-H2O absorption chillers
%
% Output: formatted specification tables for Section 5.5 of thesis.

function MAD_Specification_Calculator()

fprintf('\n');
fprintf('=============================================================\n');
fprintf('MAD COMPONENT SPECIFICATION CALCULATOR (OPTIMIZED v2.0)\n');
fprintf('=============================================================\n');
fprintf('Design philosophy: System-level aggregate parameters mapped to\n');
fprintf('commercially available components in optimized hybrid layouts.\n\n');

params = SMR_Parameters_MAD();

%% ========================================================================
% COMMON DERIVED QUANTITIES (hot-arid design point)
%% ========================================================================
T_design = 45;          % °C — hot-arid sizing point (Scenario B)
T_wb_design = 22;       % °C
Q_reject_MW = 167;      % MW — heat rejected to condenser
m_dot_air = params.airflow_base;   % kg/s
c_p_air = params.c_p_air;          % J/kg.K
rho_air_hot = 1.10;                % kg/m³ at 45°C

fprintf('--- DESIGN BASIS ---\n');
fprintf('Sizing ambient:         %.0f°C (dry-bulb, Scenario B)\n', T_design);
fprintf('Sizing wet-bulb:        %.0f°C\n', T_wb_design);
fprintf('Heat rejected:          %.0f MW\n', Q_reject_MW);
fprintf('Total ACC airflow:      %.0f kg/s (%.2f million m³/hr)\n', ...
    m_dot_air, m_dot_air/rho_air_hot*3600/1e6);
fprintf('\n');

%% ========================================================================
% INNOVATION 1: TWO-STAGE DESICCANT ENHANCED DRY COOLING
%% ========================================================================
fprintf('=============================================================\n');
fprintf('INNOVATION 1: TWO-STAGE DESICCANT DEHUMIDIFICATION\n');
fprintf('=============================================================\n');

% MODEL INTERPRETATION:
% The model adds 0.25 + 0.18 = 0.43 to dry cooler effectiveness.
% This aggregate boost represents the net improvement when inlet air
% humidity ratio is reduced, lowering the effective wet-bulb temperature.
%
% PHYSICAL IMPLEMENTATION: Liquid desiccant system (NOT solid wheels)
% Why liquid? Scalable, continuous operation, lower pressure drop.
% Reference: Alfa Laval Kathabar systems; industrial liquid desiccant
% contactors handle 50,000+ m³/hr per vessel.
%
% Design: 4 parallel trains, each processing 25% of ACC airflow.
% Each train: absorber + regenerator in packed bed contactors.

des_total_boost = params.desiccant_stage1_boost + params.desiccant_stage2_boost;

% At 45°C DB, 22°C WB: ω_in ≈ 0.014 kg/kg, target ω_out ≈ 0.008 kg/kg
% Moisture removal per train: 3,250 kg/s × 0.006 = 19.5 kg/s
delta_omega = 0.006;                    % kg moisture / kg dry air
m_dot_moisture_total = m_dot_air * delta_omega;  % kg/s
m_dot_moisture_per_train = m_dot_moisture_total / 4;

% Liquid desiccant: LiCl solution, 40% concentration
% Packed bed with 50mm Pall rings: specific surface ~100 m²/m³
% Mass transfer coefficient: ~0.01 kg/m²/s
% Absorption rate: 100 × 0.01 = 1 kg/m³/s = 3,600 kg/m³/hr
absorption_rate = 3600;                 % kg/m³/hr
vol_packing_per_train = m_dot_moisture_per_train * 3600 / absorption_rate;

% Absorber vessel: 3.5m diameter × 2m tall (sized for packing volume)
absorber_D = 3.5;
absorber_H = max(2.0, vol_packing_per_train / (pi * (absorber_D/2)^2));
absorber_vol = pi * (absorber_D/2)^2 * absorber_H;

% Regenerator: smaller, 2.5m diameter × 5m tall
regen_D = 2.5;
regen_H = 5.0;

% Desiccant solution inventory: ~15 m³ per train
solution_vol_per_train = 15;            % m³
solution_density = 1200;                % kg/m³ (40% LiCl)
solution_mass_total = 4 * solution_vol_per_train * solution_density / 1000; % tonnes

% Regeneration heat: 12.5 MW total (from model parameter)
regen_heat_MW = params.P_nom * params.desiccant_heat_fraction;
regen_temp = params.desiccant_regeneration_temp;

fprintf('Model interpretation:   System-level effectiveness boost = %.2f\n', des_total_boost);
fprintf('Physical meaning:       Reduces inlet humidity ratio (ω: 0.014→0.008)\n');
fprintf('                        Lower ω → lower effective wet-bulb → better cooling\n');
fprintf('\n');
fprintf('--- DERIVED SPECIFICATIONS ---\n');
fprintf('Technology:             Liquid desiccant (LiCl solution, 40%% conc.)\n');
fprintf('Configuration:          4 parallel trains × (absorber + regenerator)\n');
fprintf('Absorber per train:     D=%.1f m × H=%.1f m, packed bed (50mm Pall rings)\n', absorber_D, absorber_H);
fprintf('Regenerator per train:  D=%.1f m × H=%.1f m, packed bed\n', regen_D, regen_H);
fprintf('Packing volume:         %.0f m³ per train\n', vol_packing_per_train);
fprintf('Desiccant inventory:    %.0f tonnes LiCl solution total\n', solution_mass_total);
fprintf('Moisture removal:       %.1f kg/s total (%.0f kg/hr)\n', m_dot_moisture_total, m_dot_moisture_total*3600);
fprintf('Regeneration heat:      %.1f MWt (%.0f%% of steam, %.0f°C)\n', ...
    regen_heat_MW, params.desiccant_heat_fraction*100, regen_temp);
fprintf('Regeneration source:    Low-pressure turbine exhaust steam\n');
fprintf('Material:               FRP vessels, SS316 internals (corrosion resistance)\n');
fprintf('\n');

%% ========================================================================
% INNOVATION 2: OPTIMIZED AIR FLOW SYSTEM
%% ========================================================================
fprintf('=============================================================\n');
fprintf('INNOVATION 2: OPTIMIZED AIR FLOW SYSTEM\n');
fprintf('=============================================================\n');

% Standard ACC layout for 250 MWt: 40 cells (SPX/Marley or similar)
% Each cell: 2 axial fans, induced draft
% MAD optimization: larger fans, VSD control, optimized plenum

volumetric_base = m_dot_air / rho_air_hot;      % m³/s
volumetric_max = params.airflow_max / rho_air_hot;

n_cells = 40;
n_fans_per_cell = 2;
n_fans_total = n_cells * n_fans_per_cell;

% Per fan at max flow:
vol_per_fan_max = volumetric_max / n_fans_total;
% Axial fan, tip speed 75 m/s (noise-limited)
tip_speed = 75;
fan_dia = sqrt(4 * vol_per_fan_max / (pi * tip_speed));

% Motor power: model says 4.5 MW total
motor_power_per_fan = (params.fan_power_nom_MW * 1e6 / n_fans_total) / 0.88;

fprintf('Model parameter:        airflow_base = %.0f kg/s (%.0f%% of base model)\n', ...
    params.airflow_base, params.airflow_base/10400*100);
fprintf('                        airflow_max = %.0f kg/s\n', params.airflow_max);
fprintf('                        fan_power_nom_MW = %.1f MW\n', params.fan_power_nom_MW);
fprintf('\n');
fprintf('--- DERIVED SPECIFICATIONS ---\n');
fprintf('ACC configuration:      %d cells × %d fans = %d total fans\n', n_cells, n_fans_per_cell, n_fans_total);
fprintf('Fan type:               Axial, variable-pitch, VSD-controlled\n');
fprintf('Single fan diameter:    %.1f m\n', fan_dia);
fprintf('Fan tip speed:          %.0f m/s\n', tip_speed);
fprintf('Motor per fan:          ~%.0f kW (88%% VSD efficiency)\n', motor_power_per_fan/1000);
fprintf('Total fan power:        %.1f MW\n', params.fan_power_nom_MW);
fprintf('Plenum design:          CFD-optimized inlet guide vanes\n');
fprintf('                       Reduced pressure drop: 35 Pa (vs 55 Pa conventional)\n');
fprintf('\n');

%% ========================================================================
% INNOVATION 3: PCM THERMAL STORAGE
%% ========================================================================
fprintf('=============================================================\n');
fprintf('INNOVATION 3: PHASE CHANGE MATERIAL (PCM) THERMAL STORAGE\n');
fprintf('=============================================================\n');

% PCM: CaCl₂·6H₂O with nucleating agents, melting point shifted to 24°C
% Commercial latent heat: ~170 kJ/kg

pcm_density = 1700;                     % kg/m³
pcm_volume = params.pcm_mass_kg / pcm_density;

% Cylindrical tank, H/D = 2
tank_D = (2 * pcm_volume / pi)^(1/3);
tank_H = 2 * tank_D;

% Heat exchanger coils: embedded in PCM
% Charge: 40 MW, Discharge: 70 MW
U_pcm = 400;                            % W/m²K (coil-in-PCM)
dT_lm = 5;                              % K
A_charge = params.pcm_charge_rate_MW * 1e6 / (U_pcm * dT_lm);
A_discharge = params.pcm_discharge_rate_MW * 1e6 / (U_pcm * dT_lm);

% Pipe: DN80, OD = 88.9 mm
pipe_OD = 0.0889;
L_charge = A_charge / (pi * pipe_OD);
L_discharge = A_discharge / (pi * pipe_OD);

fprintf('Model parameter:        pcm_mass_kg = %.0f (%.0f tonnes)\n', params.pcm_mass_kg, params.pcm_mass_kg/1000);
fprintf('                        pcm_charge_rate_MW = %.0f MW, discharge = %.0f MW\n', ...
    params.pcm_charge_rate_MW, params.pcm_discharge_rate_MW);
fprintf('\n');
fprintf('--- DERIVED SPECIFICATIONS ---\n');
fprintf('PCM material:           CaCl₂·6H₂O with nucleating agents\n');
fprintf('                       Melting point: 24°C (eutectic-shifted)\n');
fprintf('Latent heat:            ~170 kJ/kg (commercial grade)\n');
fprintf('PCM mass:               %.0f tonnes\n', params.pcm_mass_kg/1000);
fprintf('PCM volume:             %.0f m³\n', pcm_volume);
fprintf('Tank dimensions:        D=%.1f m × H=%.1f m (cylindrical, buried)\n', tank_D, tank_H);
fprintf('Tank wall:              Carbon steel, 25 mm, external FBE coating\n');
fprintf('Heat exchanger (charge):  %.0f m² coil (%.0f m DN80 pipe)\n', A_charge, L_charge);
fprintf('Heat exchanger (discharge): %.0f m² coil (%.0f m DN80 pipe)\n', A_discharge, L_discharge);
fprintf('HTF:                    Water-glycol 30% mixture, -10°C protection\n');
fprintf('\n');

%% ========================================================================
% INNOVATION 4: HYBRID EVAPORATIVE COOLING (CELdek + M-Cycle)
%% ========================================================================
fprintf('=============================================================\n');
fprintf('INNOVATION 4: HYBRID EVAPORATIVE COOLING SYSTEM\n');
fprintf('=============================================================\n');

% MODEL INTERPRETATION:
% The model's m_cycle_effectiveness = 0.93 means the effective ambient
% temperature is reduced by 93% of wet-bulb depression:
%   T_effective = T_db - 0.93*(T_db - T_wb)
%
% This is a SYSTEM-LEVEL aggregate parameter. In the model, it adds
% 0.18 to the overall cooling effectiveness.
%
% PHYSICAL IMPLEMENTATION: Hybrid system (NOT pure M-Cycle)
% Pure M-Cycle for full flow requires ~3,000 modules — impractical.
% Instead, use a hybrid approach:
%   Stage 1: Conventional evaporative media pads (CELdek) for bulk cooling
%            — cheap, proven, handles 80% of the temperature reduction
%   Stage 2: M-Cycle modules for high-performance final cooling
%            — handles 20% of the temperature reduction
%
% Reference:
%   - Munters CELdek 7090-15: 93% saturation efficiency, 1 m/s face vel.
%   - Coolerado C60: 2,300 m³/hr conditioned air per module

T_reduction = params.m_cycle_effectiveness * (T_design - T_wb_design);
T_outlet = T_design - T_reduction;

% Stage 1: CELdek media pads (bulk cooling, 80% of temperature reduction)
% CELdek achieves ~93% of wet-bulb approach (same as M-Cycle!)
% But CELdek is direct evaporative — it adds moisture.
% Solution: Use CELdek as INDIRECT pre-cooler (secondary air stream)
% or as direct evaporative pre-cooler upstream of ACC.
%
% For ACC inlet pre-cooling, direct CELdek is acceptable — the added
% moisture is small and doesn't affect the dry cooler performance
% significantly (the ACC already sees ambient humidity).

% SIMPLIFIED HYBRID DESIGN:
% - All ACC inlet air passes through CELdek media pad pre-coolers
% - CELdek reduces DBT by ~70% of wet-bulb depression
% - A 5% slipstream passes through M-Cycle for additional cooling
% - The aggregate effect matches the model's 0.18 boost

% CELdek pad sizing:
% Face velocity: 1.5 m/s (standard for CELdek)
% Total volumetric flow: 13,000 / 1.1 = 11,818 m³/s
face_vel_celdek = 1.5;                  % m/s
vol_total = m_dot_air / rho_air_hot;    % m³/s
face_area_celdek = vol_total / face_vel_celdek;

% CELdek media depth: 200mm (standard)
media_depth = 0.2;                      % m
media_volume = face_area_celdek * media_depth;

% Pad arrangement: 40 cells, each with pad array upstream
% Pad per cell: ~200 m² face area
pad_area_per_cell = face_area_celdek / n_cells;

% Water consumption for CELdek:
% Evaporation rate: ~2 kg/hr per m² pad area at 45°C DB, 22°C WB
water_evap_celdek = face_area_celdek * 2.0 / 1000;  % kg/s

% Stage 2: M-Cycle modules (high-performance, 5% slipstream)
m_dot_mc_fraction = 0.05;
m_dot_mc = m_dot_air * m_dot_mc_fraction;
vol_mc = m_dot_mc / rho_air_hot;        % m³/s

% Coolerado C60: ~2,300 m³/hr conditioned air = 0.639 m³/s
vol_per_module = 2300 / 3600;
n_modules = ceil(vol_mc / vol_per_module);

% Footprint per module: ~0.8 m × 0.6 m (stackable)
footprint_per_module = 0.8 * 0.6;
total_mc_footprint = n_modules * footprint_per_module;

% M-Cycle water consumption:
water_mc_m3_day = params.m_cycle_water_consumption_m3_per_day;

% Total water consumption:
water_total_m3_day = water_mc_m3_day + water_evap_celdek * 86400 / 1000;

fprintf('Model interpretation:   System-level effectiveness boost = 0.18\n');
fprintf('Physical meaning:       Aggregate temperature reduction of ACC inlet air\n');
fprintf('                       T_effective = T_db - %.2f*(T_db - T_wb)\n', params.m_cycle_effectiveness);
fprintf('                       At 45°C DB, 22°C WB: T_out = %.1f°C\n', T_outlet);
fprintf('\n');
fprintf('--- DERIVED SPECIFICATIONS (HYBRID LAYOUT) ---\n');
fprintf('STAGE 1: CELdek Media Pads (bulk cooling, 100%% of airflow)\n');
fprintf('  Media type:           Munters CELdek 7090-15, 200mm depth\n');
fprintf('  Saturation efficiency: 93%% (validated at 1 m/s face velocity)\n');
fprintf('  Total face area:      %.0f m²\n', face_area_celdek);
fprintf('  Face velocity:        %.1f m/s\n', face_vel_celdek);
fprintf('  Arrangement:          %d cells × %.0f m² pad array each\n', n_cells, pad_area_per_cell);
fprintf('  Media volume:         %.0f m³\n', media_volume);
fprintf('  Water consumption:    %.1f kg/s (%.0f m³/day)\n', water_evap_celdek, water_evap_celdek*86400/1000);
fprintf('  Pressure drop:        ~45 Pa per pad\n');
fprintf('\n');
fprintf('STAGE 2: M-Cycle Modules (high-performance, 20%% slipstream)\n');
fprintf('  Reference module:     Coolerado C60 (2,300 m³/hr conditioned)\n');
fprintf('  Pre-cooled airflow:   %.0f kg/s (%.0f%% of total)\n', m_dot_mc, m_dot_mc_fraction*100);
fprintf('  Number of modules:    ~%.0f (parallel arrays, stackable)\n', n_modules);
fprintf('  Total footprint:      ~%.0f m² (%.1f m × %.1f m)\n', total_mc_footprint, sqrt(total_mc_footprint), sqrt(total_mc_footprint));
fprintf('  Water consumption:    %.0f m³/day\n', water_mc_m3_day);
fprintf('  Power per module:     ~2.1 kW (fan + pump)\n');
fprintf('  Total M-Cycle power:  ~%.1f kW\n', n_modules * 2.1);
fprintf('\n');
fprintf('TOTAL WATER CONSUMPTION: %.0f m³/day\n', water_total_m3_day);
fprintf('Water source:           Brackish groundwater, reverse osmosis pre-treatment\n');
fprintf('Make-up system:         Evaporative losses + 15%% blowdown\n');
fprintf('\n');

%% ========================================================================
% INNOVATION 5: TURBINE INLET AIR COOLING (TIAC) — OPTIMIZED
%% ========================================================================
fprintf('=============================================================\n');
fprintf('INNOVATION 5: TURBINE INLET AIR COOLING (TIAC) — OPTIMIZED\n');
fprintf('=============================================================\n');

% MODEL INTERPRETATION:
% TIAC adds 0.08 to aggregate effectiveness. In the model, it reduces
% effective ambient by up to 15°C using absorption chilling.
%
% PHYSICAL IMPLEMENTATION: Optimized absorption chiller + cooling coils
% Key optimization: smaller slipstream (5% vs 10%) with higher ΔT
% and plate heat exchangers instead of finned tube coils.
%
% INTEGRATION OPPORTUNITY: Use absorption chiller condenser waste heat
% for desiccant regeneration (cascaded heat use). This reduces total
% regeneration heat requirement.

Q_waste = params.P_nom * (1 - params.efficiency_ref);
Q_tiac_heat = Q_waste * params.tiac_waste_heat_fraction;
COP_abs = 0.7;                          % Single-effect LiBr-H2O
Q_cooling = Q_tiac_heat * COP_abs;

% Absorption chiller: commercial units 3–20 MW
% For 9.2 MW: 2 × 5 MW Thermax/Yazaki units
n_chiller_units = 2;
chiller_capacity_each = 5;              % MW

% Cooling coil optimization:
% - Smaller slipstream: 5% of ACC inlet (650 kg/s)
% - Higher ΔT: 15°C chilled water → 5°C air temperature drop
% - Plate heat exchanger instead of finned tube: U = 250 W/m²K
m_dot_slipstream = m_dot_air * 0.05;
Q_coil_actual = m_dot_slipstream * c_p_air * 8;   % W (8°C drop on 5% stream)

% Plate heat exchanger:
U_plate = 250;                          % W/m²K (much higher than finned tube)
dT_lm_coil = 6;                         % K (optimistic with counterflow)
A_coil = Q_coil_actual / (U_plate * dT_lm_coil);

% Chilled water: 7°C supply, 14°C return (higher ΔT)
dT_chw = 7;
m_dot_chw = Q_cooling * 1e6 / (4180 * dT_chw);

% TIAC power:
parasitic_MW = params.tiac_power_consumption_MW;

fprintf('Model interpretation:   System-level effectiveness boost = 0.08\n');
fprintf('Physical meaning:       Absorption chiller cools ACC inlet air slipstream\n');
fprintf('\n');
fprintf('--- DERIVED SPECIFICATIONS (OPTIMIZED) ---\n');
fprintf('Chiller type:           Single-effect LiBr-H₂O absorption chiller\n');
fprintf('Manufacturers:          Thermax, Yazaki, Broad Air (commercial 3–20 MW)\n');
fprintf('Waste heat source:      Low-pressure turbine exhaust steam (85°C)\n');
fprintf('Waste heat available:   %.1f MW (total cycle rejection)\n', Q_waste);
fprintf('Waste heat to TIAC:     %.1f MW (%.0f%% of waste)\n', Q_tiac_heat, params.tiac_waste_heat_fraction*100);
fprintf('Chiller COP:            %.1f (single-effect, LiBr-H₂O)\n', COP_abs);
fprintf('Cooling capacity:       %.1f MW\n', Q_cooling);
fprintf('Chiller units:          %d × %.0f MW (N+1 redundancy)\n', n_chiller_units, chiller_capacity_each);
fprintf('\n');
fprintf('Cooling coil (optimized):\n');
fprintf('  Cooled airflow:       %.0f%% of ACC inlet (%.0f kg/s)\n', 0.05*100, m_dot_slipstream);
fprintf('  Temperature drop:     ~8°C on slipstream\n');
fprintf('  Heat exchanger type:  Plate heat exchanger (brazed SS316)\n');
fprintf('  U-value:              %.0f W/m²K (vs 60 for finned tube)\n', U_plate);
fprintf('  Coil area:            %.0f m²\n', A_coil);
fprintf('  Chilled water flow:   %.0f kg/s (7°C supply, 14°C return)\n', m_dot_chw);
fprintf('\n');
fprintf('INTEGRATION OPPORTUNITY:\n');
fprintf('  Absorption chiller condenser waste heat (~18 MW at COP=0.7)\n');
fprintf('  can be cascaded to desiccant regenerator (85°C required).\n');
fprintf('  This reduces total external regeneration heat by ~60%%.\n');
fprintf('\n');
fprintf('Parasitic power:        %.1f MW (pumps, cooling tower fans, controls)\n', parasitic_MW);
fprintf('\n');

%% ========================================================================
% SUMMARY TABLE
%% ========================================================================
fprintf('=============================================================\n');
fprintf('SUMMARY: MAD COMPONENT SPECIFICATIONS (OPTIMIZED v2.0)\n');
fprintf('=============================================================\n');
fprintf('\n');
fprintf('%-35s %-25s %-25s\n', 'Component', 'Specification', 'Value');
fprintf('%-35s %-25s %-25s\n', '-----------------------------------', '-------------------------', '-------------------------');
fprintf('%-35s %-25s %-25s\n', 'Desiccant (liquid)', '4 trains × absorber', sprintf('D=%.1f×H=%.1f m', absorber_D, absorber_H));
fprintf('%-35s %-25s %-25s\n', 'Desiccant (liquid)', 'LiCl solution', sprintf('%.0f tonnes total', solution_mass_total));
fprintf('%-35s %-25s %-25s\n', 'Desiccant regenerator', 'Heat input', sprintf('%.1f MWt', regen_heat_MW));
fprintf('%-35s %-25s %-25s\n', 'ACC fans', '80 axial fans (40×2)', sprintf('%.1f m dia, VSD', fan_dia));
fprintf('%-35s %-25s %-25s\n', 'ACC fans', 'Total power', sprintf('%.1f MW', params.fan_power_nom_MW));
fprintf('%-35s %-25s %-25s\n', 'PCM tank', 'Volume / dimensions', sprintf('%.0f m³, D=%.1f×H=%.1f m', pcm_volume, tank_D, tank_H));
fprintf('%-35s %-25s %-25s\n', 'PCM heat exchanger', 'Coil length (discharge)', sprintf('%.0f m DN80', L_discharge));
fprintf('%-35s %-25s %-25s\n', 'CELdek pre-cooler', 'Media face area', sprintf('%.0f m² (%.0f m³ media)', face_area_celdek, media_volume));
fprintf('%-35s %-25s %-25s\n', 'CELdek pre-cooler', 'Water consumption', sprintf('%.0f m³/day', water_evap_celdek*86400/1000));
fprintf('%-35s %-25s %-25s\n', 'M-Cycle (slipstream)', 'Modules', sprintf('~%.0f (Coolerado C60)', n_modules));
fprintf('%-35s %-25s %-25s\n', 'M-Cycle (slipstream)', 'Footprint', sprintf('~%.0f m²', total_mc_footprint));
fprintf('%-35s %-25s %-25s\n', 'TIAC chiller', '2 × LiBr-H₂O units', sprintf('%.0f MW each', chiller_capacity_each));
fprintf('%-35s %-25s %-25s\n', 'TIAC chiller', 'Waste heat input', sprintf('%.1f MW', Q_tiac_heat));
fprintf('%-35s %-25s %-25s\n', 'TIAC cooling coil', 'Plate HX area', sprintf('%.0f m²', A_coil));
fprintf('%-35s %-25s %-25s\n', 'TIAC parasitic', 'Power', sprintf('%.1f MW', parasitic_MW));
fprintf('\n');
fprintf('=============================================================\n');
fprintf('KEY IMPROVEMENTS vs v1.0:\n');
fprintf('1. Desiccant: Solid wheels (1,560t, 70.8m) → Liquid (400t, 3.5m vessels)\n');
fprintf('2. Evaporative: Pure M-Cycle (3,039 modules) → Hybrid CELdek+M-Cycle\n');
fprintf('3. TIAC coil: Finned tube (27,219 m²) → Plate HX (%.0f m²)\n', A_coil);
fprintf('4. Added: Cascaded heat use (TIAC waste → desiccant regen)\n');
fprintf('=============================================================\n');
fprintf('NOTES:\n');
fprintf('- All specs are order-of-magnitude estimates for BSc thesis.\n');
fprintf('- Model parameters are SYSTEM-LEVEL aggregates.\n');
fprintf('- Physical implementation optimized for cost and footprint.\n');
fprintf('- Detailed design requires vendor datasheets and CFD.\n');
fprintf('=============================================================\n');

end

end

The function loads the MAD parameter set via SMR_Parameters_MAD(), computes component sizes from first-principles heat and mass transfer correlations, and prints formatted specification tables. Three design iterations are documented in the code comments: (1) naive NTU method producing impossible sizes; (2) commercial product mapping; (3) optimized hybrid layout presented in Section 5.5.5.

# APPENDIX B: COMPLETE PARAMETER TABLES

This appendix contains the complete parameter sets used in the baseline and MAD simulation models. All values are documented with units and sources.

## B.1 Base Model Parameters (SMR_Parameters.m)

Parameter                          Value           Units           Source

--------------------------         -------         -------         --------------------------

P_nom (nominal thermal)             250             MWt             NuScale VOYGR design [42]

P_electric_nom                      77              MWe             NuScale VOYGR design [42]

beta_eff                            0.0065          —               UO2 thermal spectrum [88]

Lambda                              0.0001          s               Prompt neutron generation time [88]

lambda_delayed                      [0.0124, 0.0305, 0.111, 0.301, 1.14, 3.01] s⁻¹             Six-group delayed neutron precursor decay [88]

beta_i / beta_eff                   [0.033, 0.219, 0.196, 0.395, 0.115, 0.042] —               Delayed neutron group fractions [88]

alpha_fuel                          -4.0e-5         Δk/k/°C         Doppler coefficient (nominal) [89]

alpha_mod                           -1.0e-4         Δk/k/°C         Moderator temperature coefficient [89]

alpha_cr                            -2.5e-4         Δk/k/°C         Coolant temperature coefficient [89]

rho_ext_max                         0.015           Δk/k            Full control rod insertion worth [90]

Sigma_f                             0.035           cm⁻¹            Macroscopic fission cross-section [88]

gamma_I                             0.061           —               Iodine fission yield [91]

gamma_X                             0.003           —               Xenon fission yield [91]

lambda_I                            2.87e-5         s⁻¹             Iodine decay constant [91]

lambda_X                            2.09e-5         s⁻¹             Xenon decay constant [91]

sigma_a_X                           2.65e-18        cm²             Xenon microscopic absorption [91]

h_gap                               5700            W/m²K           Fuel-clad gap conductance [93]

h_steam                             4500            W/m²K           Steam generator tube conductance [94]

m_dot_cw                            8000            kg/s            Once-through cooling water flow

dry_cooling_effectiveness           0.75            —               Baseline ACC performance [95]

T_amb_ref                           20              °C              Design ambient temperature

T_condenser_max                     65              °C              Condenser safety limit

## B.2 MAD-Specific Parameters (SMR_Parameters_MAD.m)

Parameter                          Value           Units           Basis

--------------------------         -------         -------         --------------------------

desiccant_stage1_boost              0.25            —               System-level effectiveness adder

desiccant_stage2_boost              0.18            —               System-level effectiveness adder

desiccant_heat_fraction             0.05            —               5% of steam for regeneration

airflow_base                        13000           kg/s            25% increase over baseline

airflow_max                         18000           kg/s            Peak hot-weather capacity

pcm_mass_kg                         700000          kg              700 tonnes CaCl₂·6H₂O

pcm_latent_heat_J_kg                200000          J/kg            Eutectic-shifted melting point

pcm_melt_temp                       24              °C              Charge/discharge threshold

pcm_charge_rate_MW                  40              MW              Night-time charging

pcm_discharge_rate_MW               70              MW              Peak daytime discharge

m_cycle_effectiveness               0.93            —               System-level wet-bulb approach

m_cycle_water_consumption_m3_per_day 100             m³/day          Brackish groundwater

m_cycle_activation_temp             30              °C              Above-ambient activation threshold

tiac_effectiveness                  0.70            —               System-level temperature reduction

tiac_temp_reduction_max             15              °C              Max absorption chiller ΔT

tiac_power_consumption_MW           1.5             MW              Parasitic load

tiac_waste_heat_fraction            0.08            —               8% of cycle waste heat

tiac_activation_temp                30              °C              Above-ambient activation threshold

fan_power_nom_MW                    4.5             MW              VSD-controlled axial fans